{"text_format":"3","workbook":"xlsx","n_sheets":2,"sheets":["保养年计划","Sheet3"],"read":"whole","date_system":"1900"}

{"sheet":"保养年计划","index":0,"n_rows":377,"n_cols":13,"rows_kept":377,"merged":[[0,0,0,2],[1,0,1,12],[2,0,2,12],[3,0,4,0],[3,1,4,1],[3,2,4,2],[3,3,3,7],[3,8,3,12],[5,1,12,1],[13,1,16,1],[17,1,19,1],[20,1,31,1],[32,1,37,1],[38,1,43,1],[44,1,63,1],[64,1,65,1],[66,1,87,1],[88,1,91,1],[92,1,98,1],[99,1,109,1],[110,1,123,1],[124,1,141,1],[142,1,189,1],[190,1,201,1],[202,1,209,1],[210,1,237,1],[238,1,246,1],[247,1,262,1],[263,1,271,1],[272,1,289,1],[312,1,321,1],[322,1,350,1],[351,1,358,1],[359,1,376,1]]}
["附件三："]
["六圩污水处理厂设备保养年计划表"]
["2019年"]
["序号","安装地点","设备名称","一级保养",{"$nulls":4},"二级保养"]
[{"$nulls":3},"保养内容","油品","用量","保养周期","第一次保养月份","保养内容","油品","用量","保养周期","第一次保养月份"]
[1,"一期进水泵房","1#进水泵","检查线缆、吊链、叶轮",null,null,"1年","5月"]
[2,null,"2#进水泵","检查线缆、吊链、叶轮",null,null,"1年","5月"]
[3,null,"3#进水泵","检查线缆、吊链、叶轮",null,null,"1年","5月"]
[4,null,"4#进水泵","检查线缆、吊链、叶轮",null,null,"1年","5月"]
[5,null,"1#进水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[6,null,"2#进水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[7,null,"1#粗格栅进水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[8,null,"2#粗格栅进水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[9,"一期粗格栅间","1#粗格栅","轴承润滑","锂基脂","适量","3个月","1月","减速箱换油","CKC220中级压工业齿轮油","4L/台","1年","3月"]
[10,null,"2#粗格栅","轴承润滑","锂基脂","适量","3个月","1月","减速箱换油","CKC220中级压工业齿轮油","4L/台","1年","3月"]
[11,null,"1#螺旋输送机","轴承润滑","锂基脂","适量","3个月","1月"]
[12,null,"2#螺旋输送机","轴承润滑","锂基脂","适量","3个月","1月","减速箱换油","CKC220中级压工业齿轮油","3L/台","1年","3月"]
[13,"一期细格栅间","1#细格栅","轴承润滑","锂基脂","适量","3个月","1月","减速箱换油","CKC220中级压工业齿轮油","4L/台","1年","3月"]
[14,null,"2#细格栅","轴承润滑","锂基脂","适量","3个月","1月","减速箱换油","CKC220中级压工业齿轮油","4L/台","1年","3月"]
[15,null,"螺旋输送机","轴承润滑","锂基脂","适量","3个月","1月","减速箱换油","CKC220中级压工业齿轮油","3L/台","1年","3月"]
[16,"一期旋流沉砂池","1#罗茨风机","过滤器清灰、轴承润滑","锂基脂","适量","3个月","1月","齿轮箱换油","壳牌可耐压S2G  220","4L/台","1年","4月"]
[17,null,"2#罗茨风机","过滤器清灰、轴承润滑","锂基脂","适量","3个月","1月","齿轮箱换油","壳牌可耐压S2G  220","4L/台","1年","4月"]
[18,null,"1#砂水分离器","轴承润滑","锂基脂","适量","3个月","1月"]
[19,null,"2#砂水分离器","轴承润滑","锂基脂","适量","3个月","1月"]
[20,null,"1#搅拌器","轴承润滑","锂基脂","适量","3个月","1月"]
[21,null,"2#搅拌器","轴承润滑","锂基脂","适量","3个月","1月"]
[22,null,"1#进水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[23,null,"2#进水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[24,null,"1#出水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[25,null,"2#出水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[26,null,"1#超越闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[27,null,"2#超越闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[28,"1#氧化沟","1#表曝机","轴承润滑","锂基脂","适量","3个月","1月","齿轮箱换油","CKC220中级压工业齿轮油","95L/台","1年","6月"]
[29,null,"2#表曝机","轴承润滑","锂基脂","适量","3个月","1月","齿轮箱换油","CKC220中级压工业齿轮油","95L/台","1年","6月"]
[30,null,"3#表曝机","轴承润滑","锂基脂","适量","3个月","1月","齿轮箱换油","CKC220中级压工业齿轮油","95L/台","1年","6月"]
[31,null,"1#推流器","检查线缆、吊链、叶轮",null,null,"1年","4月"]
[32,null,"2#推流器","检查线缆、吊链、叶轮",null,null,"1年","4月"]
[33,null,"3#推流器","检查线缆、吊链、叶轮",null,null,"1年","4月"]
[34,"2#氧化沟","1#表曝机","轴承润滑","锂基脂","适量","3个月","1月","齿轮箱换油","CKC220中级压工业齿轮油","95L/台","1年","6月"]
[35,null,"2#表曝机","轴承润滑","锂基脂","适量","3个月","1月","齿轮箱换油","CKC220中级压工业齿轮油","95L/台","1年","6月"]
[36,null,"3#表曝机","轴承润滑","锂基脂","适量","3个月","1月","齿轮箱换油","CKC220中级压工业齿轮油","95L/台","1年","6月"]
[37,null,"1#推流器","检查线缆、吊链、叶轮",null,null,"1年","4月"]
[38,null,"2#推流器","检查线缆、吊链、叶轮",null,null,"1年","4月"]
[39,null,"3#推流器","检查线缆、吊链、叶轮",null,null,"1年","4月"]
[40,"一期二沉池","1#单管吸泥机（西北）","轴承润滑","锂基脂","适量","3个月","2月"]
[41,null,"2#单管吸泥机（东北）","轴承润滑","锂基脂","适量","3个月","2月"]
[42,null,"3#单管吸泥机（西南）","轴承润滑","锂基脂","适量","3个月","2月"]
[43,null,"4#单管吸泥机（东南）","轴承润滑","锂基脂","适量","3个月","2月"]
[44,null,"1#套筒阀","丝杆润滑","锂基脂","适量","3个月","2月"]
[45,null,"2#套筒阀","丝杆润滑","锂基脂","适量","3个月","2月"]
[46,null,"3#套筒阀","丝杆润滑","锂基脂","适量","3个月","2月"]
[47,null,"4#套筒阀","丝杆润滑","锂基脂","适量","3个月","2月"]
[48,null,"1#排渣阀门","丝杆润滑","锂基脂","适量","3个月","2月"]
[49,null,"2#排渣阀门","丝杆润滑","锂基脂","适量","3个月","2月"]
[50,null,"3#排渣阀门","丝杆润滑","锂基脂","适量","3个月","2月"]
[51,null,"4#排渣阀门","丝杆润滑","锂基脂","适量","3个月","2月"]
[52,null,"1#出水闸门","丝杆润滑","锂基脂","适量","3个月","2月"]
[53,null,"2#出水闸门","丝杆润滑","锂基脂","适量","3个月","2月"]
[54,null,"3#出水闸门","丝杆润滑","锂基脂","适量","3个月","2月"]
[55,null,"4#出水闸门","丝杆润滑","锂基脂","适量","3个月","2月"]
[56,null,"1#进水闸门","丝杆润滑","锂基脂","适量","3个月","2月"]
[57,null,"2#进水闸门","丝杆润滑","锂基脂","适量","3个月","2月"]
[58,null,"3#进水闸门","丝杆润滑","锂基脂","适量","3个月","2月"]
[59,null,"4#进水闸门","丝杆润滑","锂基脂","适量","3个月","2月"]
[60,"一期加药间","1#隔膜计量泵",{"$nulls":5},"减速箱换油","美孚630","15L/台","2年","8月"]
[61,null,"2#隔膜计量泵",{"$nulls":5},"减速箱换油","美孚630","15L/台","2年","8月"]
[62,"二期进水泵房","1#进水泵","检查线缆、吊链、叶轮",null,null,"1年","5月"]
[63,null,"2#进水泵","检查线缆、吊链、叶轮",null,null,"1年","5月"]
[64,null,"3#进水泵","检查线缆、吊链、叶轮",null,null,"1年","5月"]
[65,null,"4#进水泵","检查线缆、吊链、叶轮",null,null,"1年","5月"]
[66,null,"5#进水泵","检查线缆、吊链、叶轮",null,null,"1年","5月"]
[67,null,"6#进水泵","检查线缆、吊链、叶轮",null,null,"1年","5月"]
[68,null,"7#进水泵","检查线缆、吊链、叶轮",null,null,"1年","5月"]
[69,null,"1#粗格栅进水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[70,null,"2#粗格栅进水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[71,null,"3#粗格栅进水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[72,null,"1#粗格栅出水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[73,null,"2#粗格栅出水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[74,null,"3#粗格栅出水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[75,null,"1#联通闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[76,null,"1#细格栅进水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[77,null,"2#细格栅进水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[78,null,"3#细格栅进水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[79,null,"4#细格栅进水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[80,null,"1#细格栅出水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[81,null,"2#细格栅出水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[82,null,"3#细格栅出水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[83,null,"4#细格栅出水闸门","丝杆润滑","锂基脂","适量","3个月","1月"]
[84,"二期粗格栅间","1#粗格栅","轴承润滑","锂基脂","适量","3个月","1月","减速箱换油","CKC220中级压工业齿轮油","4L/台","1年","3月"]
[85,null,"2#粗格栅","轴承润滑","锂基脂","适量","3个月","1月","减速箱换油","CKC220中级压工业齿轮油","4L/台","1年","3月"]
[86,null,"3#粗格栅","轴承润滑","锂基脂","适量","3个月","1月","减速箱换油","CKC220中级压工业齿轮油","4L/台","1年","3月"]
[87,null,"螺旋输送机","轴承润滑","锂基脂","适量","3个月","1月","减速箱换油","CKC220中级压工业齿轮油","3L/台","1年","3月"]
[88,"二期细格栅间","1#细格栅","轴承润滑","锂基脂","适量","3个月","1月","减速箱换油","CKC220中级压工业齿轮油","4L/台","1年","4月"]
[89,null,"2#细格栅","轴承润滑","锂基脂","适量","3个月","1月","减速箱换油","CKC220中级压工业齿轮油","4L/台","1年","4月"]
[90,null,"3#细格栅","轴承润滑","锂基脂","适量","3个月","1月","减速箱换油","CKC220中级压工业齿轮油","4L/台","1年","4月"]
[91,null,"4#细格栅","轴承润滑","锂基脂","适量","3个月","1月","减速箱换油","CKC220中级压工业齿轮油","4L/台","1年","4月"]
[92,null,"螺旋压榨机","轴承润滑","锂基脂","适量","3个月","1月","减速箱换油","CKC220中级压工业齿轮油","2L/台","1年","4月"]
[93,null,"1#细格栅冲洗水泵","轴承润滑","锂基脂","适量","3个月","1月"]
[94,null,"2#细格栅冲洗水泵","轴承润滑","锂基脂","适量","3个月","1月"]
[95,"二期旋流沉砂池","1#罗茨风机","过滤器清灰、轴承润滑","锂基脂","适量","3个月","1月","齿轮箱换油","壳牌可耐压S2G  220","4L/台","1年","4月"]
[96,null,"2#罗茨风机","过滤器清灰、轴承润滑","锂基脂","适量","3个月","1月","齿轮箱换油","壳牌可耐压S2G  220","4L/台","1年","4月"]
[97,null,"1#砂水分离器","轴承润滑","锂基脂","适量","3个月","1月"]
[98,null,"2#砂水分离器","轴承润滑","锂基脂","适量","3个月","1月"]
[99,null,"1#搅拌器","轴承润滑","锂基脂","适量","3个月","1月"]
[100,null,"2#搅拌器","轴承润滑","锂基脂","适量","3个月","1月"]
[101,null,"1#进水闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[102,null,"2#进水闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[103,null,"1#出水闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[104,null,"2#出水闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[105,null,"超越闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[106,"初沉池","1#刮泥机","轴承润滑","锂基脂","适量","3个月","1月","减速箱换油","CKC220中级压工业齿轮油","60L/台","2年","5月"]
[107,null,"2#刮泥机","轴承润滑","锂基脂","适量","3个月","1月","减速箱换油","CKC220中级压工业齿轮油","60L/台","2年","5月"]
[108,null,"1#粉碎机","轴承润滑","锂基脂","适量","3个月","1月"]
[109,null,"2#粉碎机","轴承润滑","锂基脂","适量","3个月","1月"]
[110,null,"1#排泥泵","轴承润滑","锂基脂","适量","3个月","1月"]
[111,null,"2#排泥泵","轴承润滑","锂基脂","适量","3个月","1月"]
[112,null,"1#电动闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[113,null,"2#电动闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[114,null,"3#电动闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[115,null,"4#电动闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[116,null,"5#电动闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[117,null,"6#电动闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[118,null,"7#电动闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[119,null,"8#电动闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[120,"二期水解池","1#进水闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[121,null,"2#进水闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[122,null,"3#进水闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[123,null,"4#进水闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[124,null,"5#进水闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[125,null,"6#进水闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[126,null,"7#进水闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[127,null,"8#进水闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[128,null,"9#进水闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[129,null,"10#进水闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[130,null,"1#空气闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[131,null,"2#空气闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[132,null,"3#空气闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[133,null,"4#空气闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[134,null,"5#空气闸门","轴承润滑","锂基脂","适量","3个月","1月"]
[135,null,"1#罗茨风机","过滤器清灰、轴承润滑","锂基脂","适量","3个月","1月"]
[136,null,"2#罗茨风机","过滤器清灰、轴承润滑","锂基脂","适量","3个月","1月"]
[137,null,"3#罗茨风机","过滤器清灰、轴承润滑","锂基脂","适量","3个月","1月"]
[138,"二期生物池","1#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[139,null,"2#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[140,null,"3#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[141,null,"4#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[142,null,"5#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[143,null,"6#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[144,null,"7#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[145,null,"8#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[146,null,"9#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[147,null,"10#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[148,null,"1#外回流进口闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[149,null,"2#外回流进口闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[150,null,"1#内回流闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[151,null,"2#内回流闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[152,null,"3#内回流闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[153,null,"4#内回流闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[154,null,"5#内回流闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[155,null,"6#内回流闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[156,null,"7#内回流闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[157,null,"8#内回流闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[158,null,"1#外回流泵房闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[159,null,"2#外回流泵房闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[160,null,"1#空气闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[161,null,"2#空气闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[162,null,"3#空气闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[163,null,"4#空气闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[164,null,"5#空气闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[165,null,"6#空气闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[166,null,"1#推流器","检查线缆、吊链、叶轮",null,null,"1年","9月"]
[167,null,"2#推流器","检查线缆、吊链、叶轮",null,null,"1年","9月"]
[168,null,"3#推流器","检查线缆、吊链、叶轮",null,null,"1年","9月"]
[169,null,"4#推流器","检查线缆、吊链、叶轮",null,null,"1年","9月"]
[170,null,"5#推流器","检查线缆、吊链、叶轮",null,null,"1年","9月"]
[171,null,"6#推流器","检查线缆、吊链、叶轮",null,null,"1年","9月"]
[172,null,"7#推流器","检查线缆、吊链、叶轮",null,null,"1年","9月"]
[173,null,"8#推流器","检查线缆、吊链、叶轮",null,null,"1年","9月"]
[174,null,"9#推流器","检查线缆、吊链、叶轮",null,null,"1年","9月"]
[175,null,"10#推流器","检查线缆、吊链、叶轮",null,null,"1年","9月"]
[176,null,"11#推流器","检查线缆、吊链、叶轮",null,null,"1年","10月"]
[177,null,"12#推流器","检查线缆、吊链、叶轮",null,null,"1年","10月"]
[178,null,"13#推流器","检查线缆、吊链、叶轮",null,null,"1年","10月"]
[179,null,"14#推流器","检查线缆、吊链、叶轮",null,null,"1年","10月"]
[180,null,"15#推流器","检查线缆、吊链、叶轮",null,null,"1年","10月"]
[181,null,"16#推流器","检查线缆、吊链、叶轮",null,null,"1年","10月"]
[182,null,"17#推流器","检查线缆、吊链、叶轮",null,null,"1年","10月"]
[183,null,"18#推流器","检查线缆、吊链、叶轮",null,null,"1年","10月"]
[184,null,"19#推流器","检查线缆、吊链、叶轮",null,null,"1年","10月"]
[185,null,"20#推流器","检查线缆、吊链、叶轮",null,null,"1年","10月"]
[186,"鼓风机房","1#电动离心鼓风机",{"$nulls":5},"更换冷却风过滤器",null,null,"3个月","3月"]
[{"$nulls":3},"进风口过滤器清灰",null,null,"3个月","3月","更换进风口过滤器",null,null,"6个月","3月"]
[187,null,"2#电动离心鼓风机",{"$nulls":5},"更换冷却风过滤器",null,null,"3个月","3月"]
[{"$nulls":3},"进风口过滤器清灰",null,null,"3个月","3月","更换进风口过滤器",null,null,"6个月","3月"]
[188,null,"3#电动离心鼓风机",{"$nulls":5},"更换冷却风过滤器",null,null,"3个月","3月"]
[{"$nulls":3},"进风口过滤器清灰",null,null,"3个月","3月","更换进风口过滤器",null,null,"6个月","3月"]
[189,null,"4#电动离心鼓风机",{"$nulls":5},"更换冷却风过滤器",null,null,"3个月","3月"]
[{"$nulls":3},"进风口过滤器清灰",null,null,"3个月","3月","更换进风口过滤器",null,null,"6个月","3月"]
[190,null,"5#电动离心鼓风机",{"$nulls":5},"更换冷却风过滤器",null,null,"3个月","3月"]
[{"$nulls":3},"进风口过滤器清灰",null,null,"3个月","3月","更换进风口过滤器",null,null,"6个月","3月"]
[191,null,"6#电动离心鼓风机",{"$nulls":5},"更换冷却风过滤器",null,null,"3个月","3月"]
[{"$nulls":3},"进风口过滤器清灰",null,null,"3个月","3月","更换进风口过滤器",null,null,"6个月","3月"]
[192,"二期二沉池","1#单管吸泥机（西）","轴承润滑","锂基脂","适量","3个月","3月"]
[193,null,"2#单管吸泥机（东）","轴承润滑","锂基脂","适量","3个月","3月"]
[194,null,"1#套筒阀","轴承润滑","锂基脂","适量","3个月","3月"]
[195,null,"2#套筒阀","轴承润滑","锂基脂","适量","3个月","3月"]
[196,null,"1#排渣阀门","轴承润滑","锂基脂","适量","3个月","3月"]
[197,null,"2#排渣阀门","轴承润滑","锂基脂","适量","3个月","3月"]
[198,null,"1#出水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[199,null,"2#出水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[200,"高密度沉淀池","1#偏心螺杆泵（回）"]
[201,null,"2#偏心螺杆泵（回）"]
[202,null,"3#偏心螺杆泵（回）"]
[203,null,"4#偏心螺杆泵（回）"]
[204,null,"1#偏心螺杆泵（排）"]
[205,null,"2#偏心螺杆泵（排）"]
[206,null,"3#偏心螺杆泵（排）"]
[207,null,"4#偏心螺杆泵（排）"]
[208,null,"1#垂直轴机械搅拌器（混合）",{"$nulls":5},"减速箱换油","46#机械油","2L/台","1年","8月"]
[209,null,"2#垂直轴机械搅拌器（混合）",{"$nulls":5},"减速箱换油","46#机械油","2L/台","1年","8月"]
[210,null,"3#垂直轴机械搅拌器（混合）",{"$nulls":5},"减速箱换油","46#机械油","2L/台","1年","8月"]
[211,null,"4#垂直轴机械搅拌器（混合）",{"$nulls":5},"减速箱换油","46#机械油","2L/台","1年","8月"]
[212,null,"1#垂直轴机械搅拌器（絮凝）",{"$nulls":5},"减速箱换油","46#机械油","2L/台","1年","8月"]
[213,null,"2#垂直轴机械搅拌器（絮凝）",{"$nulls":5},"减速箱换油","46#机械油","2L/台","1年","8月"]
[214,null,"3#垂直轴机械搅拌器（絮凝）",{"$nulls":5},"减速箱换油","46#机械油","2L/台","1年","8月"]
[215,null,"4#垂直轴机械搅拌器（絮凝）",{"$nulls":5},"减速箱换油","46#机械油","2L/台","1年","8月"]
[216,null,"5#垂直轴机械搅拌器（絮凝）",{"$nulls":5},"减速箱换油","46#机械油","2L/台","1年","8月"]
[217,null,"6#垂直轴机械搅拌器（絮凝）",{"$nulls":5},"减速箱换油","46#机械油","2L/台","1年","8月"]
[218,null,"7#垂直轴机械搅拌器（絮凝）",{"$nulls":5},"减速箱换油","46#机械油","2L/台","1年","8月"]
[219,null,"8#垂直轴机械搅拌器（絮凝）",{"$nulls":5},"减速箱换油","46#机械油","2L/台","1年","8月"]
[220,null,"1#刮泥机","轴承润滑","锂基脂","适量","3个月","3月"]
[221,null,"2#刮泥机","轴承润滑","锂基脂","适量","3个月","3月"]
[222,null,"3#刮泥机","轴承润滑","锂基脂","适量","3个月","3月"]
[223,null,"4#刮泥机","轴承润滑","锂基脂","适量","3个月","3月"]
[224,null,"1#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[225,null,"2#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[226,null,"3#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[227,null,"4#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[228,"二期加药间","1#隔膜计量泵"]
[229,null,"2#隔膜计量泵"]
[230,null,"3#隔膜计量泵"]
[231,null,"4#隔膜计量泵"]
[232,null,"5#隔膜计量泵"]
[233,null,"6#隔膜计量泵"]
[234,null,"1#偏心螺杆泵",{"$nulls":5},"油室换油","壳牌可耐压S2G  220","适量","2年","8月"]
[235,null,"2#偏心螺杆泵",{"$nulls":5},"油室换油","壳牌可耐压S2G  220","适量","2年","8月"]
[236,null,"3#偏心螺杆泵",{"$nulls":5},"油室换油","壳牌可耐压S2G  220","适量","2年","8月"]
[237,"微滤机池","1#微滤机","轴承润滑","锂基脂","适量","3个月","3月"]
[238,null,"2#微滤机","轴承润滑","锂基脂","适量","3个月","3月"]
[239,null,"3#微滤机","轴承润滑","锂基脂","适量","3个月","3月"]
[240,null,"4#微滤机","轴承润滑","锂基脂","适量","3个月","3月"]
[241,null,"5#微滤机","轴承润滑","锂基脂","适量","3个月","3月"]
[242,null,"6#微滤机","轴承润滑","锂基脂","适量","3个月","3月"]
[243,null,"1#微滤机进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[244,null,"2#微滤机进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[245,null,"3#微滤机进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[246,null,"4#微滤机进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[247,null,"5#微滤机进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[248,null,"6#微滤机进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[249,null,"1#总进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[250,null,"2#总进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[251,null,"1#出水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[252,null,"2#出水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[253,"三期水解池","1#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[254,null,"2#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[255,null,"3#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[256,null,"4#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[257,null,"5#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[258,null,"6#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[259,null,"1#空气闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[260,null,"2#空气闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[261,null,"3#空气闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[262,"三期生物池","1#空气闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[263,null,"2#空气闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[264,null,"3#空气闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[265,null,"4#空气闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[266,null,"5#空气闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[267,null,"6#空气闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[268,null,"1#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[269,null,"2#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[270,null,"3#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[271,null,"4#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[272,null,"5#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[273,null,"6#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[274,null,"1#外回流闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[275,null,"2#外回流闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[276,null,"1#内回流闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[277,null,"2#内回流闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[278,null,"3#内回流闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[279,null,"4#内回流闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[280,null,"1#推流器","检查线缆、吊链、叶轮",null,null,"1年","6月"]
[281,null,"2#推流器","检查线缆、吊链、叶轮",null,null,"1年","6月"]
[282,null,"3#推流器","检查线缆、吊链、叶轮",null,null,"1年","6月"]
[283,null,"4#推流器","检查线缆、吊链、叶轮",null,null,"1年","6月"]
[284,null,"5#推流器","检查线缆、吊链、叶轮",null,null,"1年","6月"]
[285,null,"6#推流器","检查线缆、吊链、叶轮",null,null,"1年","6月"]
[286,null,"7#推流器","检查线缆、吊链、叶轮",null,null,"1年","6月"]
[287,null,"8#推流器","检查线缆、吊链、叶轮",null,null,"1年","6月"]
[288,null,"9#推流器","检查线缆、吊链、叶轮",null,null,"1年","6月"]
[289,null,"10#推流器","检查线缆、吊链、叶轮",null,null,"1年","6月"]
[290,null,"11#推流器","检查线缆、吊链、叶轮",null,null,"1年","6月"]
[291,null,"12#推流器","检查线缆、吊链、叶轮",null,null,"1年","7月"]
[292,null,"13#推流器","检查线缆、吊链、叶轮",null,null,"1年","7月"]
[293,null,"14#推流器","检查线缆、吊链、叶轮",null,null,"1年","7月"]
[294,null,"15#推流器","检查线缆、吊链、叶轮",null,null,"1年","7月"]
[295,null,"16#推流器","检查线缆、吊链、叶轮",null,null,"1年","7月"]
[296,null,"17#推流器","检查线缆、吊链、叶轮",null,null,"1年","7月"]
[297,null,"18#推流器","检查线缆、吊链、叶轮",null,null,"1年","7月"]
[298,null,"19#推流器","检查线缆、吊链、叶轮",null,null,"1年","7月"]
[299,null,"20#推流器","检查线缆、吊链、叶轮",null,null,"1年","7月"]
[300,null,"21#推流器","检查线缆、吊链、叶轮",null,null,"1年","7月"]
[301,null,"21#推流器","检查线缆、吊链、叶轮",null,null,"1年","7月"]
[302,"三期二沉池","1#单管吸泥机（西）","轴承润滑","锂基脂","适量","3个月","3月"]
[303,null,"2#单管吸泥机（东）","轴承润滑","锂基脂","适量","3个月","3月"]
[304,null,"1#套筒阀","轴承润滑","锂基脂","适量","3个月","3月"]
[305,null,"2#套筒阀","轴承润滑","锂基脂","适量","3个月","3月"]
[306,null,"1#排渣阀门","轴承润滑","锂基脂","适量","3个月","3月"]
[307,null,"2#排渣阀门","轴承润滑","锂基脂","适量","3个月","3月"]
[308,null,"1#出水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[309,null,"2#出水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[310,null,"1#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[311,null,"2#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[312,"深床滤池","1#搅拌器","轴承润滑","锂基脂","适量","3个月","3月"]
[313,null,"2#搅拌器","轴承润滑","锂基脂","适量","3个月","3月"]
[314,null,"3#搅拌器","轴承润滑","锂基脂","适量","3个月","3月"]
[315,null,"1#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[316,null,"2#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[317,null,"3#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[318,null,"4#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[319,null,"5#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[320,null,"6#进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[321,null,"1#排污闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[322,null,"2#排污闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[323,null,"3#排污闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[324,null,"4#排污闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[325,null,"5#排污闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[326,null,"6#排污闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[327,null,"1#出水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[328,null,"2#出水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[329,null,"3#出水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[330,null,"4#出水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[331,null,"5#出水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[332,null,"6#出水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[333,null,"深床进水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[334,null,"深床超越闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[335,null,"清水池出水闸门","轴承润滑","锂基脂","适量","3个月","3月"]
[336,null,"1#罗茨风机","过滤器清灰、轴承润滑","锂基脂","适量","3个月","3月"]
[337,null,"2#罗茨风机","过滤器清灰、轴承润滑","锂基脂","适量","3个月","3月"]
[338,null,"3#罗茨风机","过滤器清灰、轴承润滑","锂基脂","适量","3个月","3月"]
[339,null,"1#推流器","检查线缆、吊链、叶轮",null,null,"1年","4月"]
[340,null,"2#推流器","检查线缆、吊链、叶轮",null,null,"1年","4月"]
[341,"三期加药间","1#隔膜计量泵（PAC)",{"$nulls":5},"减速箱换油","美孚630","15L/台","2年","5月"]
[342,null,"2#隔膜计量泵（PAC)",{"$nulls":5},"减速箱换油","美孚630","15L/台","2年","5月"]
[343,null,"3#隔膜计量泵（PAC)",{"$nulls":5},"减速箱换油","美孚630","15L/台","2年","5月"]
[344,null,"1#隔膜计量泵（碳源)"]
[345,null,"2#隔膜计量泵（碳源)"]
[346,null,"3#隔膜计量泵（碳源)",{"$nulls":5},"减速箱换油","美孚630","15L/台","2年","5月"]
[347,null,"4#隔膜计量泵（碳源)",{"$nulls":5},"减速箱换油","美孚630","15L/台","2年","5月"]
[348,null,"5#隔膜计量泵（碳源)",{"$nulls":5},"减速箱换油","美孚630","15L/台","2年","5月"]
[349,"脱水机房","1#偏心螺杆泵（污泥泵）",{"$nulls":5},"油室换油","壳牌可耐压S2G  220","适量","2年","6月"]
[350,null,"2#偏心螺杆泵（污泥泵）"]
[351,null,"3#偏心螺杆泵（污泥泵）",{"$nulls":5},"油室换油","壳牌可耐压S2G  220","适量","2年","6月"]
[352,null,"1#偏心螺杆泵（PAM）",{"$nulls":5},"油室换油","壳牌可耐压S2G  220","适量","2年","6月"]
[353,null,"2#偏心螺杆泵（PAM）",{"$nulls":5},"油室换油","壳牌可耐压S2G  220","适量","2年","6月"]
[354,null,"3#偏心螺杆泵（PAM）",{"$nulls":5},"油室换油","壳牌可耐压S2G  220","适量","2年","6月"]
[355,null,"1#粉碎机","轴承润滑","锂基脂","适量","3个月","3月"]
[356,null,"2#粉碎机","轴承润滑","锂基脂","适量","3个月","3月"]
[357,null,"3#粉碎机","轴承润滑","锂基脂","适量","3个月","3月"]
[358,null,"1#离心脱水机","螺旋轴承润滑","专用锂基脂",null,"2个月","3月","反驱动齿轮","美孚630","2L/台","6个月","6月"]
[359,null,"2#离心脱水机","螺旋轴承润滑","专用锂基脂",null,"2个月","3月","反驱动齿轮","美孚630","2L/台","6个月","6月"]
[360,null,"3#离心脱水机","螺旋轴承润滑","专用锂基脂",null,"2个月","3月","反驱动齿轮","美孚630","2L/台","6个月","6月"]
[361,null,"1#柱塞泵"]
[362,null,"2#柱塞泵"]
[363,null,"横向螺旋输送机","轴承润滑","锂基脂","适量","3个月","3月","减速箱换油","CKC220中级压工业齿轮油","3L/台","1年","6月"]
[364,null,"纵向螺旋输送机","轴承润滑","锂基脂","适量","3个月","3月","减速箱换油","CKC220中级压工业齿轮油","3L/台","1年","6月"]
[365,null,"储泥池1#推流器","检查线缆、吊链、叶轮",null,null,"1年","4月"]
[366,null,"储泥池2#推流器","检查线缆、吊链、叶轮",null,null,"1年","4月"]

{"sheet":"Sheet3","index":1,"n_rows":0,"n_cols":0,"rows_kept":0}